## Seismic Design Category B
RESPONSIBILITY MATRIX
FOR THE SEISMIC PROTECTION OF NONSTRUCTURAL COMPONENTS
SEISMIC DESIGN CATEGORY B
NONSTRUCTURAL COMPONENTS
| General categories shown with sample entries (in blue); insert line items for project specific components | Is Seismic Design Required? (yes/exempt) | Component Importance Factor, Ip (See Note 1) | Party Responsible for Design of Seismic Details (See Note 2) | Party Responsible for Preparation of Seismic Shop Drawings (See Note 2) | Party Responsible for Preparation of Seismic Calculations (See Note 2) | Is Special Seismic Certification Required? (See Note 3) (yes/no) | Is seismic design being handled as a Deferred Approval? | Party Responsible for Site Inspection of Installed Component/System
ITEM | DESIGNATED SEISMIC SYSTEMS (See Note 1) | Exempt | Ip=1.5 |  |  |  | No
S.1 | Component required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways. (per 13.1.3.1) | Exempt per 13.1.4.2
S.2 | Component conveys, supports or contains toxic or explosive substances. (per 13.1.3.2) | Exempt per 13.1.4.2
S.3 | Component in or attached to Risk Category IV structure and is needed for continued operation of the facility or its failure could impair the continued operation of the facility. (see 13.2.3) | NA
Note | Key Exemptions for Designated Seismic Systems in Seismic Design Category B (other exemptions may apply, see ASCE 7-10) | Exempt
| Mechanical and electrical components in Seismic Design Category B are exempt from the requirements of Chapter 13 of ASCE 7. | Exempt per 13.1.4
ITEM | STANDARD NONSTRUCTURAL COMPONENTS |  | Ip=1.0 (UON)
ARCHITECTURAL COMPONENTS
A.1 | Exterior Wall Components | Exempt
A.2 | Interior Partitions | Exempt
A.3 | Ceilings | Exempt
A.4 | Parapets and Appendages | Yes | 1 |  |  |  | No
Parapet supported by bearing or shear wall
A.5 | Canopies, marquees, signs | Exempt
A.6 | Chimneys, stacks | Exempt
A.7 | Stairways | Exempt
A.8 | Site walls, fences | Exempt
Note | Key Exemptions for Architectural components in Category B (other exemptions may apply, see ASCE 7-10) | Exempt
| Architectural components in Seismic Design Category B are exempt from the requirements of Chapter 13 of ASCE 7 with the exception of parapets supported by bearing walls or shear walls. | Exempt per 13.5.6
MECHANICAL & PLUMBING COMPONENTS
B.1 | Air-side HVAC Equipment | Exempt
B.2 | Wet-Side HVAC Equipment | Exempt
B.3 | HVAC Piping and Valves | Exempt
B.4 | Ductwork | Exempt
B.5 | Storage Tanks, Pressure Vessels | Exempt
B.6 | Medical Gas equipment and piping | Exempt
B.7 | Plumbing equipment and piping | Exempt
B.8 | Fire Suppression equipment and piping | Exempt
B.9 | Pneumatic Systems | Exempt
ELECTRICAL COMPONENTS
C.1 | Electrical Equipment | Exempt
C.2 | Electrical Distribution Equipment | Exempt
C.3 | Light Fixtures | Exempt
C.4 | Communication Systems | Exempt
TRANSPORTATION COMPONENTS
D.1 | Conveyance systems and equipment | Exempt
FURNITURE, FIXTURES & EQUIPMENT (FF&E) AND CONTENTS
E.1 | Shelving, storage racks | Exempt
E.2 | Televisions, monitors | Exempt
E.3 | Desktop computers | Exempt
E.4 | Computer and communication racks, cabinets and boards | Exempt
E.5 | Kitchen equipment | Exempt
E.6 | Demountable partitions | Exempt
E.7 | Access floors | Exempt
E.8 | Shelf and counter mounted contents or equipment | Exempt
E.9 | Specialty equipment | Exempt
Note | Key Exemptions for FF&E and Contents in Category B (other exemptions may apply, see ASCE 7-10)
| Furniture, cabinets and free-standing partitions 6' or less in height, are not regulated by building code. Similarly, counter- and shelf-mounted contents are not regulated by building code. The need for seismic protection of these items should be considered on a case-by-case basis in a manner consistent with the project seismic performance objectives. | Exempt
Note 1: | Definition per ASCE 7-10. DESIGNATED SEISMIC SYSTEMS: The seismic force resisting system and those architectural, electrical, and mechanical systems or their components that require design in accordance with Chapter 13 and for which the component Importance factor, Ip, is greater than 1.0. |  |  | Note 3: | 13.2.2 Certifications shall be provided for designated seismic systems assigned to Seismic Design Categories C through F as follows:
| 13.1.3 Component Importance Factor. All components shall be assigned a component importance factor as indicated in this section. The component importance factor, Ip, shall be taken as 1.5 if any of the following conditions apply: |  |  |  | 1. Active mechanical and electrical equipment that must remain operable following the design earthquake ground motion shall be certified by the manufacturer as operable whereby active parts or energized components shall be certified exclusively on the basis of approved shake table testing in accordance with ASCE 7-10 Section 13.2.5 or experience data in accordance with Section 13.2.6 unless it can be shown that the component is inherently rugged by comparison with similar seismically qualified components. Evidence demonstrating compliance with this requirement shall be submitted for approval to the authority having jurisdiction after review and acceptable by a registered design professional.
1. The component is required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways.
2. The component conveys, supports or otherwise contains toxic, highly toxic or explosive substances where the quantity of materials exceeds a threshold quantity established by the authority having jurisdiction and is sufficient to pose a threat to the public if released.
| 3. The component is in or attached to a Risk Category IV structure and it is needed for continued operation of the facility or its failure could impair the continued operation of the facility. |  |  |  | 2. Components with hazardous substances and assigned a component importance factor, Ip of 1.5 in accordance what ASCE 7-10 Section 13.1.3 shall be certified by the manufacturer as maintaining containment following the design earthquake ground motion by (1) analysis, (2) approved shake table testing in accordance with Section13.2.5, or (3) experience data in accordance with Section 13.2.6. Evidence demonstrating compliance with this requirement shall be submitted for approval to the authority having jurisdiction after review and acceptance by a registered design professional.
The component conveys, supports or otherwise contains hazardous substances and is attached to a structure or portion thereof classified by the authority havihng jurisdiction as a hazardous occupancy.
All other components shall be assigned a component importance
factor, Ip, equal to 1.0.
Note 2: | "Seismic details, shop drawings and calculations" refer to the design of supports, anchorages, braces, restraints and fastenings that connect the nonstructural component or system to the structure.

## Seismic Design Category C
RESPONSIBILITY MATRIX
FOR THE SEISMIC PROTECTION OF NONSTRUCTURAL COMPONENTS
SEISMIC DESIGN CATEGORY C
NONSTRUCTURAL COMPONENTS
| General categories shown with sample entries (in blue); insert line items for project specific components | Is Seismic Design Required? (yes/exempt) | Component Importance Factor, Ip (See Note 1) | Party Responsible for Design of Seismic Details (See Note 2) | Party Responsible for Preparation of Seismic Shop Drawings (See Note 2) | Party Responsible for Preparation of Seismic Calculations (See Note 2) | Is Special Seismic Certification Required? (See Note 3) (yes/no) | Is seismic design being handled as a Deferred Approval? | Party Responsible for Site Inspection of Installed Component/System
ITEM | DESIGNATED SEISMIC SYSTEMS (See Note 1) | Yes | Ip=1.5 |  |  |  | Yes
S.1 | Component required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways. (per 13.1.3.1) | Yes | 1.5 |  |  |  | Yes
Fire protection sprinkler system
Egress stairways not part of the building structure
S.2 | Component conveys, supports or contains toxic or explosive substances. (per 13.1.3.2) | Yes | 1.5 |  |  |  | Yes
Natural gas piping over 1" nominal diameter and trapeze-supported natural gas piping where the total weight supported by the trapeze assembly exceeds 10 plf.
S.3 | Component in or attached to Risk Category IV structure and is needed for continued operation of the facility or its failure could impair the continued operation of the facility. (see 13.2.3) | Yes | 1.5 |  |  |  | Yes
Smoke evacuation ducts
Smoke evacuation fan
Emergency generators including engine/generator, enclosure, engine start batteries, exhaust system, fuel oil day tank, fuel oil storage tank, fuel oil piping
Emergency switchgear
Emergency electrical distribution panels
Emergency light fixtures
Electrical cable/conduit/cable tray carrying emergency power over 2.5 inch nominal diamter and trapeze-supported conduit or bundled cabling where the total weight supported by the trapeze assemply or hanger exceeds 10 plf
Fire pump
Fire sprinkler piping
Fire alarm control panel
HVAC supply and return ductwork containing toxic or explosive substances including components in-line with duct system
Elevator and related components
Note | Key Exemptions for Designated Seismic Systems in Seismic Design Category C (other exemptions may apply, see ASCE 7-10) | Exempt
| Piping exempt if (1) it is supported on a trapeze, no single pipe exceeds 2" nominal pipe size and the total weight on the trapeze is less than 10 plf (13.6.8.3.1); OR (2) the pipe is suspended <12" from structure without bending in hanger rod (13.6.8.3.2); OR (3) the pipe ≤2" dia, has an Rp of 4.5 or greater and will not contact other structural or nonstructural components or is otherwise protected if contact occurs (13.6.8.3.3). | Exempt per 13.6.8.3a
| Conduit, cable tray or other electrical distribution system (raceway) is exempt if (1) it is supported on a trapeze and the total weight on the trapeze is less than 10 plf (13.6.5.6.1a); OR (2) the raceway is suspended <12" from structure without bending in hanger rod (13.6.5.6.1b); OR (3) the conduit < 2.5" dia (13.6.5.6.2). | Exempt per 13.6.5.6
ITEM | STANDARD NONSTRUCTURAL COMPONENTS |  | Ip=1.0 (UON)
ARCHITECTURAL COMPONENTS
A.1 | Exterior Wall Components | Yes | 1 |  |  |  | No
Metal stud walls
Curtainwall
Precast panels
Glazing
A.2 | Interior Partitions | Yes | 1 |  |  |  | No
Metal stud walls
Glazing
Granite veneer
A.3 | Ceilings | Yes | 1 |  |  |  | No
Suspended acoustic tile ceilings
A.4 | Parapets and Appendages | Yes | 1.5 or 1.0 |  |  |  | No
| Masonry parapet |  | 1.5
A.5 | Canopies, marquees, signs | Yes | 1 |  |  |  | No
Wall-mounted and suspended signs over 20#
A.6 | Chimneys, stacks | Yes | 1 |  |  |  | No
A.7 | Stairways | Yes | 1 |  |  |  | No
A.8 | Site walls, fences | Yes | 1 |  |  |  | No
Note | Key Exemptions for Architectural components in Category C (other exemptions may apply, see ASCE 7-10) | Exempt
| Suspended ceilings with areas less than or equal to 144 square feet that are surrounded by walls or soffits that are laterally braced to the structure above are exempt from the requirements for seismic design. | Exempt per 13.5.6
MECHANICAL & PLUMBING COMPONENTS
B.1 | Air-side HVAC Equipment | Exempt | 1
B.2 | Wet-Side HVAC Equipment | Exempt | 1
B.3 | HVAC Piping and Valves | Exempt | 1
B.4 | Ductwork | Exempt | 1
B.5 | Storage Tanks, Pressure Vessels | Exempt | 1
B.6 | Medical Gas equipment and piping | Exempt | 1
B.7 | Plumbing equipment and piping | Exempt | 1
B.8 | Fire Suppression equipment and piping | Exempt | 1
B.9 | Pneumatic Systems | Exempt | 1
ELECTRICAL COMPONENTS
C.1 | Electrical Equipment | Exempt | 1
C.2 | Electrical Distribution Equipment | Exempt | 1
C.3 | Light Fixtures | Exempt | 1
C.4 | Communication Systems | Exempt | 1
TRANSPORTATION COMPONENTS
D.1 | Conveyance systems and equipment | Exempt | 1
Elevators and related components (if not included as part of "designated seismic system")
FURNITURE, FIXTURES & EQUIPMENT (FF&E) AND CONTENTS
E.1 | Shelving, storage racks | Yes | 1 |  |  |  | No
Cabinets over 6' tall
E.2 | Televisions, monitors | Exempt
E.3 | Desktop computers | Exempt
E.4 | Computer and communication racks, cabinets and boards | Exempt
E.5 | Kitchen equipment | Exempt
E.6 | Demountable partitions | Exempt
E.7 | Access floors | Exempt
E.8 | Shelf and counter mounted contents or equipment | Exempt
E.9 | Specialty equipment | Exempt
Note | Key Exemptions for FF&E and Contents in Category C (other exemptions may apply, see ASCE 7-10)
| Furniture, cabinets and free-standing partitions 6' or less in height, are not regulated by building code. Similarly, counter- and shelf-mounted contents are not regulated by building code. The need for seismic protection of these items should be considered on a case-by-case basis in a manner consistent with the project seismic performance objectives. | Exempt
Note 1: | Definition per ASCE 7-10. DESIGNATED SEISMIC SYSTEMS: The seismic force resisting system and those architectural, electrical, and mechanical systems or their components that require design in accordance with Chapter 13 and for which the component Importance factor, Ip, is greater than 1.0. |  |  | Note 3: | 13.2.2 Certifications shall be provided for designated seismic systems assigned to Seismic Design Categories C through F as follows:
| 13.1.3 Component Importance Factor. All components shall be assigned a component importance factor as indicated in this section. The component importance factor, Ip, shall be taken as 1.5 if any of the following conditions apply: |  |  |  | 1. Active mechanical and electrical equipment that must remain operable following the design earthquake ground motion shall be certified by the manufacturer as operable whereby active parts or energized components shall be certified exclusively on the basis of approved shake table testing in accordance with ASCE 7-10 Section 13.2.5 or experience data in accordance with Section 13.2.6 unless it can be shown that the component is inherently rugged by comparison with similar seismically qualified components. Evidence demonstrating compliance with this requirement shall be submitted for approval to the authority having jurisdiction after review and acceptable by a registered design professional.
1. The component is required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways.
2. The component conveys, supports or otherwise contains toxic, highly toxic or explosive substances where the quantity of materials exceeds a threshold quantity established by the authority having jurisdiction and is sufficient to pose a threat to the public if released.
| 3. The component is in or attached to a Risk Category IV structure and it is needed for continued operation of the facility or its failure could impair the continued operation of the facility. |  |  |  | 2. Components with hazardous substances and assigned a component importance factor, Ip of 1.5 in accordance what ASCE 7-10 Section 13.1.3 shall be certified by the manufacturer as maintaining containment following the design earthquake ground motion by (1) analysis, (2) approved shake table testing in accordance with Section13.2.5, or (3) experience data in accordance with Section 13.2.6. Evidence demonstrating compliance with this requirement shall be submitted for approval to the authority having jurisdiction after review and acceptance by a registered design professional.
The component conveys, supports or otherwise contains hazardous substances and is attached to a structure or portion thereof classified by the authority havihng jurisdiction as a hazardous occupancy.
All other components shall be assigned a component importance
factor, Ip, equal to 1.0.
| Exception: For California hospitals, Ip = 1.5 for the design of supports and attachments for all nonstructural components. |  |  |  | 3. OSHPD Code Application Notice 2-1708A.5 – Certification of Equipment and Nonstructural Components, provides detailed requirements regarding equipment seismic certification for buildings under the authority of California Office of Statewide Health Pllanning and Development. This may also serve as a useful reference for projects in other jurisdictions.
Note 2: | "Seismic details, shop drawings and calculations" refer to the design of supports, anchorages, braces, restraints and fastenings that connect the nonstructural component or system to the structure.

## Seismic Design Category DEF
RESPONSIBILITY MATRIX
FOR THE SEISMIC PROTECTION OF NONSTRUCTURAL COMPONENTS
SEISMIC DESIGN CATEGORIES D, E & F
NONSTRUCTURAL COMPONENTS
| General categories shown with sample entries (in blue); insert line items for project specific components | Is Seismic Design Required? (yes/exempt) | Component Importance Factor, Ip (See Note 1) | Party Responsible for Design of Seismic Details (See Note 2) | Party Responsible for Preparation of Seismic Shop Drawings (See Note 2) | Party Responsible for Preparation of Seismic Calculations (See Note 2) | Is Special Seismic Certification Required? (See Note 3) (yes/no) | Is seismic design being handled as a Deferred Approval? | Party Responsible for Site Inspection of Installed Component/System
ITEM | DESIGNATED SEISMIC SYSTEMS (See Note 1) | Yes | Ip=1.5 |  |  |  | Yes
S.1 | Component required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways. (per 13.1.3.1) | Yes | 1.5 |  |  |  | Yes
Fire protection sprinkler system
Egress stairways not part of the building structure
S.2 | Component conveys, supports or contains toxic or explosive substances. (per 13.1.3.2) | Yes | 1.5 |  |  |  | Yes
Natural gas piping over 1" nominal diameter and trapeze-supported natural gas piping where the total weight supported by the trapeze assembly exceeds 10 plf.
Bulk oxygen tank and associated piping
S.3 | Component in or attached to Risk Category IV structure and is needed for continued operation of the facility or its failure could impair the continued operation of the facility. (see 13.2.3) | Yes | 1.5 |  |  |  | Yes
Smoke evacuation ducts
Smoke evacuation fan
Emergency generators including engine/generator, enclosure, engine start batteries, exhaust system, fuel oil day tank, fuel oil storage tank, fuel oil piping
Emergency switchgear/transformers
Emergency electrical distribution panels
Emergency light fixtures
Electrical cable/conduit/cable tray carrying emergency power over 2.5 inch nominal diameter and trapeze-supported conduit or bundled cabling where the total weight supported by the trapeze assembly for hanger exceeds 10 plf
Fire pump
Fire sprinkler piping
Fire alarm control panel
HVAC supply and return ductwork containing toxic or explosive substances including components in-line with duct system
Elevator and related components
Cooling Tower
Note | Key Exemptions for Designated Seismic Systems in Seismic Design Categories D, E & F (other exemptions may apply, see ASCE 7-10) | Exempt
| Piping exempt if (1) it is supported on a trapeze, no single pipe exceeds 1" nominal pipe size and the total weight on the trapeze is less than 10 plf (13.6.8.3.1); OR (2) the pipe is suspended <12" from structure without bending in hanger rod (13.6.8.3.2); OR (3) the pipe ≤ 1" dia, has an Rp of 4.5 or greater and will not contact other structural or nonstructural components or is otherwise protected if contact occurs (13.6.8.3.3). | Exempt per 13.6.8
| Conduit, cable tray or other electrical distribution system (raceway) is exempt if (1) it is supported on a trapeze and the total weight on the trapeze is less than 10 plf (13.6.5.6.1a); OR (2) the raceway is suspended <12" from structure without bending in hanger rod (13.6.5.6.1b); OR (3) the conduit < 2.5" dia (13.6.5.6.2). | Exempt per 13.6.5.6
ITEM | STANDARD NONSTRUCTURAL COMPONENTS |  | Ip=1.0 (UON)
ARCHITECTURAL COMPONENTS
A.1 | Exterior Wall Components | Yes | 1 |  |  |  | No
Metal stud walls
Curtainwall
Precast panels
Glazing
A.2 | Interior Partitions | Yes | 1 |  |  |  | No
Metal stud walls
Glazing
Granite veneer
A.3 | Ceilings | Yes | 1 |  |  |  | No
Suspended acoustic tile ceilings
A.4 | Parapets and Appendages | Yes | 1.5 or 1.0 |  |  |  | No
| Masonry parapet |  | 1.5
A.5 | Canopies, marquees, signs | Yes | 1 |  |  |  | No
Wall-mounted and suspended signs over 20#
A.6 | Chimneys, stacks | Yes | 1 |  |  |  | No
A.7 | Stairways | Yes | 1 |  |  |  | No
A.8 | Site walls, fences | Yes | 1 |  |  |  | No
Note | Key Exemptions for Architectural components in Categories D, E & F (other exemptions may apply, see ASCE 7-10) | Exempt
| Suspended ceilings with areas less than or equal to 144 square feet that are surrounded by walls or soffits that are laterally braced to the structure above are exempt from the requirements for seismic design. | Exempt per 13.5.6
MECHANICAL & PLUMBING COMPONENTS
B.1 | Air-side HVAC Equipment | Yes | 1 |  |  |  | No
Fans
Air handlers
Air conditioning units
Cabinet heaters
Air distribution boxes
B.2 | Wet-Side HVAC Equipment | Yes | 1
| Boilers | [5 empty] | No
Furnaces
Chillers
Water heaters
Heat exchangers
Evaporators
Air separators
B.3 | HVAC Piping and Valves | Yes | 1 |  |  |  | No
Chilled water piping
B.4 | Ductwork | Yes | 1 |  |  |  | No
Ducts over 6 sf
In-line devices weighing more than 75#
B.5 | Storage Tanks, Pressure Vessels | Yes | 1 |  |  |  | No
Expansion tanks
B.6 | Medical Gas equipment and piping | Yes | 1.5 |  |  |  | No
B.7 | Plumbing equipment and piping | Yes | 1 |  |  |  | No
Pumps
B.8 | Fire Suppression equipment and piping | Yes | 1
(typically included as part of "designated seismic system")
B.9 | Pneumatic Systems | Yes | 1 |  |  |  | No
Note | Key Exemptions for M/P Equipment in Categories D, E & F (other exemptions may apply, see code) | Exempt
| M/P component exempt if the component is positively attached to the structure, it weighs ≤400# and is mounted ≤4ft above the floor, and flexible connections are provided between the component and associated ductwork, piping or conduit. Also exempt if weight ≤20# or distribution system ≤5lb/ft, and has flex connections. | Exempt per 13.1.4.6
| Duct exempt if it does not carry hazardous materials and (1) it is <6 sq. ft. and it is protected from impact with adjacent components; OR (2) it is suspended <12" from structure; OR (3) it is trapeze-supported and the total supported weight is less than 10 plf. | Exempt per 13.6.7
| Piping exempt if (1) it is supported on a trapeze, no single pipe exceeds 3" nominal pipe size and the total weight on the trapeze is less than 10 plf (13.6.8.3.1); OR (2) the pipe is suspended <12" from structure without bending in hanger rod (13.6.8.3.2); OR (3) the pipe ≤ 1" dia, has an Rp of 4.5 or greater and will not contact other structural or nonstructural components or is otherwise protected if contact occurs (13.6.8.3.3). | Exempt per 13.6.8
ELECTRICAL COMPONENTS
C.1 | Electrical Equipment (Normal Power) | Yes | 1 |  |  |  | No
Motors
Transformers
Motor control centers
Panel boards
Switch gear
Instrumentation cabinets
C.2 | Electrical Distribution Equipment (Normal Power) | Yes | 1 |  |  |  | No
Conduit 2.5" diameter and larger
Cable tray over 10 plf
Bundled cabling over 10 plf
C.3 | Light Fixtures | Yes | 1 |  |  |  | No
Recessed
Wall-mounted and weighing more than 20#
Pendant
C.4 | Communication Systems | Yes | 1 |  |  |  | No
Panel boards
Rooftop satellite dish
Telecommunication racks and cabinets
Note | Key Exemptions for Electrical Equipment in Categories D, E & F (other exemptions may apply, see ASCE 7-10) | Exempt
| Electrical component exempt if the component is positively attached to the structure, it weighs ≤400# and is mounted ≤4ft above the floor, and flexible connections are provided between the component and associated ductwork, piping or conduit. Also exempt if weight ≤20# or distribution system ≤5lb/ft, and has flex connections. | Exempt per 13.1.4.6
| Conduit, cable tray or other electrical distribution system (raceway) is exempt if (1) it is supported on a trapeze and the total weight on the trapeze is less than 10 plf (13.6.5.6.1a); OR (2) the raceway is suspended <12" from structure without bending in hanger rod (13.6.5.6.1b); OR (3) the conduit < 2.5" dia (13.6.5.6.2). | Exempt per 13.6.5.6.1
TRANSPORTATION COMPONENTS
D.1 | Conveyance systems and equipment | Yes | 1 |  |  |  | No
Elevators and related components (if not included as part of "designated seismic system")
FURNITURE, FIXTURES & EQUIPMENT (FF&E) AND CONTENTS
E.1 | Shelving, storage racks | Yes | 1 |  |  |  | No
Bookcases, filing cabinets, storage units and similar that either (1) weigh over 400# (when filled with contents weighing 20 pcf) and are over 6' in height; or (2) have a height-to-least width ratio of 4:1 or more regardless of height
E.2 | Televisions, monitors | Yes | 1 |  |  |  | No
Wall-mounted televisions/monitors weighing over 20# (including the weight of the bracket)
E.3 | Desktop computers | Exempt4 | 1 |  |  |  | No
E.4 | Computer and communication racks, cabinets and boards | Yes | 1 |  |  |  | No
Computer cabinets
Computer racks
E.5 | Kitchen equipment | Yes | 1 |  |  |  | No
All equipment weighing over 400#
Suspended hoods
E.6 | Demountable partitions | Yes (unless exempt per ASCE 7 13.5.8.1) | 1 |  |  |  | No
All partitions over 6' in height
E.7 | Access floors | Yes | 1 |  |  |  | No
Access floors
Special access floors
E.8 | Shelf and counter mounted contents or equipment | Exempt4 | 1 |  |  |  | No
E.9 | Specialty equipment | Yes | 1 |  |  |  | No
Note | Key Exemptions for FF&E and Contents in Categories D, E & F (other exemptions may apply, see ASCE 7-10)
| Furniture, cabinets and free-standing partitions 6' or less in height, are not regulated by building code. Similarly, counter- and shelf-mounted contents are not regulated by building code. The need for seismic protection of these items should be considered on a case-by-case basis in a manner consistent with the project seismic performance objectives. | Exempt
Note 1: | Definition per ASCE 7-10. DESIGNATED SEISMIC SYSTEMS: The seismic force resisting system and those architectural, electrical, and mechanical systems or their components that require design in accordance with Chapter 13 and for which the component Importance factor, Ip, is greater than 1.0. |  |  | Note 3: | 13.2.2 Certifications shall be provided for designated seismic systems assigned to Seismic Design Categories C through F as follows:
| 13.1.3 Component Importance Factor. All components shall be assigned a component importance factor as indicated in this section. The component importance factor, Ip, shall be taken as 1.5 if any of the following conditions apply: |  |  |  | 1. Active mechanical and electrical equipment that must remain operable following the design earthquake ground motion shall be certified by the manufacturer as operable whereby active parts or energized components shall be certified exclusively on the basis of approved shake table testing in accordance with ASCE 7-10 Section 13.2.5 or experience data in accordance with Section 13.2.6 unless it can be shown that the component is inherently rugged by comparison with similar seismically qualified components. Evidence demonstrating compliance with this requirement shall be submitted for approval to the authority having jurisdiction after review and acceptable by a registered design professional.
1. The component is required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways.
2. The component conveys, supports or otherwise contains toxic, highly toxic or explosive substances where the quantity of materials exceeds a threshold quantity established by the authority having jurisdiction and is sufficient to pose a threat to the public if released.
| 3. The component is in or attached to a Risk Category IV structure and it is needed for continued operation of the facility or its failure could impair the continued operation of the facility. |  |  |  | 2. Components with hazardous substances and assigned a component importance factor, Ip of 1.5 in accordance what ASCE 7-10 Section 13.1.3 shall be certified by the manufacturer as maintaining containment following the design earthquake ground motion by (1) analysis, (2) approved shake table testing in accordance with Section13.2.5, or (3) experience data in accordance with Section 13.2.6. Evidence demonstrating compliance with this requirement shall be submitted for approval to the authority having jurisdiction after review and acceptance by a registered design professional.
The component conveys, supports or otherwise contains hazardous substances and is attached to a structure or portion thereof classified by the authority having jurisdiction as a hazardous occupancy.
All other components shall be assigned a component importance
factor, Ip, equal to 1.0.
| Exception: For California hospitals, Ip = 1.5 for the design of supports and attachments for all nonstructural components. |  |  |  | 3. OSHPD Code Application Notice 2-1708A.5 – Certification of Equipment and Nonstructural Components, provides detailed requirements regarding equipment seismic certification for buildings under the authority of California Office of Statewide Health Planning and Development. This may also serve as a useful reference for projects in other jurisdictions.
Note 2: | "Seismic details, shop drawings and calculations" refer to the design of supports, anchorages, braces, restraints and fastenings that connect the nonstructural component or system to the structure. |  |  | Note 4: | The code does not mandate restraints for counter- or shelf-mounted items. If such items are hard-wired or hard-plumbed; and/or if such items will pose a safety hazard or pose an unacceptable impact on operations if they become dislodged, restraint should be provided. The project requirement for seismic protection of these items should be clearly indicated in the contract documents.

## Basic form
RESPONSIBILITY MATRIX
FOR THE SEISMIC PROTECTION OF NONSTRUCTURAL COMPONENTS
SEISMIC DESIGN CATEGORY X
Project Name:
Project Address:
Architect:
| NONSTRUCTURAL COMPONENTS | DESIGN PHASE
| General categories shown with sample entries (in blue); insert line items for project specific components | Is Seismic Design Required? (yes/exempt) | Component Importance Factor, Ip (See Note 1) | Party Responsible for Design of Seismic Details (See Note 2) | Party Responsible for Preparation of Seismic Shop Drawings (See Note 2) | Party Responsible for Preparation of Seismic Calculations (See Note 2) | Is Special Seismic Certification Required? (See Note 3) (yes/no) | Party Responsible for Site Inspection of Installed Component/System
ITEM | DESIGNATED SEISMIC SYSTEMS (See Note 1) | Yes | Ip=1.5
S.1 | Component required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways. (per 13.1.3.1) | Yes | 1.5
| Fire protection sprinkler systems | Yes | 1.5
S.2 | Component conveys, supports or contains toxic or explosive substances. (per 13.1.3.2) | Yes | 1.5
S.3 | Component in or attached to Risk Category IV structure and is needed for continued operation of the facility or its failure could impair the continued operation of the facility. (see 13.2.3) | Yes | 1.5
Note | Exemptions for Designated Seismic Systems in Seismic Design Category B | Exempt | 1.5
ITEM | STANDARD NONSTRUCTURAL COMPONENTS |  | Ip=1.0
ARCHITECTURAL COMPONENTS
A.1 | Exterior Wall Components
A.2 | Interior Partitions
A.3 | Ceilings
A.4 | Parapets and Appendages
A.5 | Canopies, marquees, signs
A.6 | Chimneys, stacks
A.7 | Stairways
A.8 | Site walls, fences
MECHANICAL & PLUMBING COMPONENTS
B.1 | Wet-side HVAC Equipment
B.2 | Air-Side HVAC Equipment
B.3 | HVAC Piping and Valves
B.4 | Ductwork
B.5 | Storage Tanks, Pressure Vessels
B.6 | Medical Gas equipment and piping
B.7 | Plumbing equipment and piping
B.8 | Fire Suppression equipment and piping
B.9 | Pneumatic Systems
ELECTRICAL COMPONENTS
C.1 | Electrical Equipment
C.2 | Electrical Distribution Equipment
C.3 | Light Fixtures
C.4 | Communication Systems
TRANSPORTATION COMPONENTS
D.1 | Conveyance systems and equipment
FURNITURE, FIXTURES & EQUIPMENT (FF&E) AND CONTENTS
E.1 | Shelving, storage racks
E.2 | Televisions, monitors
E.3 | Desktop computers
E.4 | Computer and communication racks, cabinets and boards
E.5 | Kitchen equipment
E.6 | Demountable partitions
E.7 | Access floors
E.8 | Shelf and counter mounted contents or equipment
E.9 | Specialty equipment
Note 1:
13.1.3 | Component Importance Factor. All components shall be assigned a component importance factor as indicated in this section. The component importance factor, Ip, shall be taken as 1.5 if any of the following conditions apply:
1 | The component is required to function for life-safety purposes after an earthquake, including fire protection sprinkler systems and egress stairways.
2 | The component conveys, supports or otherwise contains toxic, highly toxic or explosive substances where the quantity of materials exceeds a threshold quantity established by the authority having jurisdiction and is sufficient to pose a threat to the public if released.
3 | The component is in or attached to a Risk Category IV structure and it is needed for continued operation of the facility or its failure could impair the continued operation of the faciity.
4 | The component conveys, supports or otherwise contains hazardous substances and is attached to a structure or portion thereof classified by the authority havihng jurisdiction as a hazardous occupancy. | [7 empty] | -
All other components shall be assigned a component importance
factor, Ip, equal to 1.0.
Note 3:
13.2.2 | Certifications shall be provided for designated seismic systems assigned to Seismic Design Cattegories C through F as follows: